## Sheet1
SCHEDULE OF RATES CONSTRUCTION OF CGS CUM COMPRESSOR STATION AT RUDRAPUR, UDHAM SINGH NAGAR (UTTARAKHAND)
ITEM NO | ITEM DESCRIPTION | UNIT | QUANTITY | Unit Rate incluisve of all taxes/duties | Total Amount
1 | EXCAVATION EXCAVATION: Excavation work by mechanical means ((Hydraulic excavator / manual means) for foundation , trench and drain in earth, soils of all types of soil, sand,graveI, and sob murum,hard rock including removing the excavated material upto a distance of 100 metres beyond the building area and stacking and spreading as directed dewatering, preparing the bed for the foundation and necessary, back filling, ramming, watering including shoring and strutting etc. upto depth of 4 Meter complete By Mechanical Means. for all Kind of Soil. | CUM | 1111.7942 |  | 0
2 | Back filling after execution of the work to proper grade and level with selected material from available excavated soil from spoil heaps with in lead of 100 MM , including re-excavated the deposited soil excavated earlier , breaking clods , laying at all depth and height in layer of thickness not exceeding 15 cm watering , roling and ramming by manual method / mechnical compactors to achieve 90 % laboratory maximum dry density , dressing , trimming etc in foundation , plinths trenchs , pits etc all complete. | CUM | 50 |  | 0
3 | BACKFILLING after execution of the WORK to proper grade and level with selected materials from available excavated soil from spoil heaps beyond a lead of 100 M and upto & inclusive of 500 M including re- excavated the deposited soil excavated earlier , breaking clods, laying at all depth and height in layer of thickness not exceeding 15 CMS , watering rolling and ramming by manual methods / mechnical compactors to achieve 90 % laboratory maximum dry density , dressing , trimming etc in foundation, plinths trenchs pits etc all complete. | CUM | 50 |  | 0
4 | SOLING SOLING: Providing soling using 80 to 120 mm size trap metal in 15 cm layer including filling voids with Crushed sand/grit,ramming watering etc. complete. | CUM | 50 |  | 0
5 | EARTH WORK FILLING EARTHWORK IN FILLING by excavating the earth from BORROW AREAS arranged by CONTRACTOR for all leads, transporting the earth from borrow area including cleaning & stripping the earth at borrow areas, breaking clods, loading, unloading and laying at all depths and heights in layers of thickness not exceeding 15 cms., watering, rolling and ramming by manual methods/mechanical compactors to achieve 90% of the maximum laboratory dry density, ressing, trimming, levelling the top surface etc. in foundations, plinths, trenches etc. all complete. | CUM | 2874 |  | 0
6 | Transporting & Disposing the SURPLUS EARTH AND DEBRIS Transporting and disposing the SURPLUS EARTH AND DEBRIS including shrubs and vegetation from construction areas to areas ANYWHERE OUTSIDE THE PLANT BOUNDARY, including re-excavating the deposited soil excavated earlier, loading, transportation, unloading, laying at all depths and heights, stacking,levelling and dressing both the area (viz. from where the earth is transported and where it is deposited) to required levels and slopes complete with all lifts as directed. For carting on the basis of truck measurements (volume of truck reduced by 30% for voids). DISPOSAL AREAS OUTSIDE PLANT BOUNDARY TO BE ARRANGED BY THE CONTRACTOR. Royalty as applicable for disposal outside plant limits to be borne by the Contractor | CUM | 100 |  | 0
7 | Provide and Laying PCC PCC - M7.5 - GRADE(1:4:8) (1 cement : 4 coarse sand: 8 graded stone aggregate 40 mm nominal size). Providing and laying in Plain cement concrete of specified grade including necessary form work (Centering & Shuttring), compacting and curing etc upto Plinth Level. complete with reversible drum type mixer/ design mix . as per direction of Engineer-in-charge. | CUM | 88.1397 |  | 0
8 | Provide and Laying PCC PCC- M10 Grade (1:3:6) (1 Cement : 4 Coarse Sand: 8 Graded stone aggregate 40 mm nominal size). Providing and laying in Plain cement concrete of specified grade including necessary form work (Centering & Shuttring), compacting and curing etc upto Plinth Level. complete with reversible drum type mixer/ design mix . as per direction of Engineer-in-charge. | CUM | 10 |  | 0
9 | Provide and Laying PCC PCC- M15 Grade (1:2:4) (1 Cement : 2 Coarse Sand: 4 Graded stone aggregatewith using 20 mm and down-size graded coarse aggregates approved quality of fine aggregates (sand) with ordinary Portland cement, included necessary form work (Centering & Shuttring), compacting and curing etc upto Plinth Level. complete with reversible drum type mixer/ design mix . as per direction of Engineer-in-charge. | CUM | 10 |  | 0
10 | RCC SUB STRUCTURE Providing and laying REINFORCED CEMENT CONCRETE OF M-25 GRADE with 20 mm and down size graded crushed stone aggregates/ gravel in SUBSTRUCTURE INCLUDING CENTERING & SHUTTERING ) e.g. foundations, raft, beams, pile caps, Retaining walls, RCC wall, counterforts, buttresses, pedestals, pipe sleepers, column, suspended floor, staricase, landings, steps, brackets etc. incuding equipments/ machine foundation & pedestrals viz MRS, generator foundation, compressor etc (Including single pour concreting as specified on the drawing) applying cement wash on concrete surface (wherever no other surface application is specified), providing bitumen coating of surface of foundation and raft, providing pockets,opening, recesses, chamfering etc. wherever required, vabrating, tamping, curing and rendering if required to give a smooth and even surface etc. (excluding the coast of Reinforcement) for all depth below and upto plinth level in any shape, position and thickness etc. all complete as specified, show and directed. ALL materials shall be supplied by contarctor. | CUM | 324.0828 |  | 0
11 | RCC SUPER STRUCTURE Providing and laying REINFORCED CEMENT CONCRETE OF M-25 GRADE with 20 mm and down size graded crushed stone aggregates/ gravel in SUPER STRUCTURE INCLUDING CENTERING & SHUTTERING in suspended floors, slabs, beams, columns, walls including counterforts, staircases, landings, steps, facias, fins, mouldings, gutters, shelves, posts, struts, equipment/ machine foundations, ramps etc. (including single pour concreting as specified on the drawing), providing cement wash (wherever no other surface application is specified), providing pockets, openings, recesses, chamfering wherever required, vibrating, tamping, curing and rendering if required to give a smooth and even surface etc. (EXCLUDING THE COST OF REINFORCEMENT) for all Heights upto & Inclusive 20 M above plinth level in any shape, position thickness etc. all complete as specified shown and directed by EIC ,. All Material shully be supplied by Contractor. | CUM | 33.363 |  | 0
12 | Concrete Pavyment |  |  |  | 0
12.1 | Providing and laying Reinforced Cement Concrete with 20mm and down size graded crushed stone aggregates in flooring, pavements etc. including leaving pockets, if necessary, making recess/drains, laying in alternate panels, etc. for all depths including shuttering, tamping, curing, etc. as specified in any shape, thickness, position and finishing the top surface smooth etc. all complete as per drawings, specifications and directions of Engineer-in-Charge. For RCC of M-30 grade concrete (all materials including cement but excluding cost of providing & fixing reinforcement and joint sealing shall be supplied by the contractor). | SQM | 1011.6 |  | 0
12.2 | Providing 20mm wide Expansion Joints in pavement slabs as per general technical specification including cleaning the joints of all loose material, filling with 20mm thick impregnated fibre boards for the full depth of slab except for 25mm depth from top and sealing the top 25mm with approved Joint Sealing Compound as per IS:1834 Type-B etc. all complete as per drawings, specifications and directions of Engineer-in-Charge
12.3 | Sealing joint around pedestal and column etc. 20mm wide x 150 mm deep including filling with 20mm thick impregnated fire board for the full depth of slab except for 25mm depth from top and sealing the top 25mm with approved joint sealing compound as per IS:1834 Type-B.
13 | WBM ROAD CONSTRUCTION |  |  |  | 0
13.1 | Preparation and consolidation of sub grade with power road roller of 8 to 12 tonne capacity after excavating earth to an average of 22.5 cm depth, dressing to camber and consolidating with road roller including making good the undulations etc. and re-rolling the sub grade and disposal of surplus earthwith lead upto 50 metres. | SQM | 1713 |  | 0
13.2 | 90 mm to 45 mm size stone aggregate | CUM | 103.2 |  | 0
13.3 | 63 mm to 45 mm size stone aggregate | CUM | 103.2 |  | 0
13.4 | 53 mm to 22.4 mm size stone aggregate | CUM | 103.2 |  | 0
13.5 | Moorum | CUM | 60 |  | 0
14 | REINFORCEMENT STEEL HYSD/TMT FE 500 Supplying and fabrication and fixing in position HYSD Steel Reinforcement /TMT Grade FE 500 of all Dia conforming to IS:1786 at all levels and position including the cost of Transportation, Straightening, Cutting, Bending Cracking, Binding, Welding, Provision of necessary charis and spacers, Preperation of bar bending scheduling, including all height and depth and getting the same approved by EIC etc. complete as per drawing and specification and including cost of binding , labour etc all complete all aspects as per scope of work deatiled construction drawing, technicial specification and direction of Engineer-In- Charge. | MT | 24.75 |  | 0
15 | PAVER BLOCK Supplying & Laying interlocking Paver Blocks for roads, footpaths and any other place etc. including providing 60 mm & 80mm thick sand filling below Paver Blocks including compaction of sand layer, filling the joints by dry sand, providing precast kerb stone of PCC M-20 at edges, including preparation of compacted sub-grade etc. all complete as per drawing, standard and directions of Engineer-in-Charge. (All material including cement supplied by contractor, paver blocks shall confirm to IS: 15658. color and shape of paver block shall be as per owner requirements for following thickness of paver blocks |  |  |  | 0
15.1 | PAVER BLOCK( Thickness - 60 mm M40 Grade) | SQ Mtr. | 100 |  | 0
15.2 | PAVER BLOCK( Thickness - 80 mm M40 Grade ) | SQ Mtr. | 702 |  | 0
16 | BRICK WORK Brick work: Provide and construction and handling over brick masonry work for Boundary wall, Rain water Drain and Tubing trench, with Burnt Brick with conventional/ I.S. type brick in cement mortar 1:6 (1Cement : 6 Coarse sand) below DPC , excavation and backfilling with service able earth, complete in all respect as per scope of work, pointing with cement motart 1:3 on exposed face and watering etc as per direction of Engineer-In- Charge upto five floor level. | CUM | 102.872 |  | 0
17 | White Cement Putty Providing and applying white cemnet based putty of averge thickness 1mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | SQ Mtr. | 565.6222 |  | 0
18 | PLASTER SAND FACED PLASTER Provide and Laying 15 MM thick cement plaster on Brick work surface in cement mortar 1:6, RCC beams, columns and chajja , Rain water drain etc. mix 1:3 (1Cement : 3 Fine Sand) with 6 MM Thick ness including making of typical grooves drip -course including hacking of RCC roof beam and column surface and curing etc. complete in all respect as per scope of work (including scaffolding etc.) and direction of Engineer- In- Charge. | SQ Mtr. | 565.6222 |  | 0
19 | Provide and Laying Paint Work (Finishing wall with Acrylic Smooth exterior paint ) Paint: Providing and applying of water proof cement paint of approved manufacture and of approved colour to the plastere surfaces including scaffolding if necessary, cleaning and preparing the surface, watering for two days etc. complete. direction of the Engineer-In-Charge.( Paint Make- Asian Paint, Berger paint, Nerolic)Two or more coats applied @ 1.67 ltr/10 sqm over and including base coat of water proffing cement paint applied @ 2.20 kg/10 sqm). | SQ Mtr. | 565.6222 |  | 0
20 | UNDERGROUND SEWER SYSTEM - RCC PIPES Supplying and laying underground R.C.C. pipes sewers with socket and spigot ends conforming to IS:458 of approved make, to proper grade and alignment, including earthwork in excavation in all types of soil except soft and hard rock for pipe trenches, etc. including dewatering, shoring and shuttering if necessary, dressing of sides, leveling, grading and ramming of bottoms, cutting the R.C.C. pipes to required lengths, lowering the pipes, jointing, including connecting the pipes to manholes and grouting the pipe body with manhole wall using cement mortar 1:2 (1 cement : 2 sand), testing, draining of water and cleaning of pipe after testing, backfilling the trenches with select material from available excavated soil including re excavating the deposited soil excavated earlier breaking clods and laying in layers of 15cm compacted thickness , watering and compacting with mechanical means like vibro rammers etc. to 90% standard proctor density as per IS:2720 Part-VII, making good the surface, including cutting of roads wherever required and making good the same, disposal of surplus earth/ unserviceable material to demarcated area anywhere within the complex limit etc. complete for all depths as per drawings, specifications and instructions of Engineer-in-Charge.(All material shall be supplied by contractor) For following Pipe size (mm) and Class(The following pipe sizes are all internal diameter of the pipes) |  |  |  | 0
20.1 | ( Dia (Internal) - 100 mm, Piping Material Class - NP2 ) | R. Mtr | 20 |  | 0
20.2 | ( Dia (Internal) - 150 mm, Piping Material Class - NP1 ) | R. Mtr | 10 |  | 0
21 | UNDERGROUND SEWER SYSTEM-HDPE PIPES :- Supplying and laying HDPE pipes conforming to IS:4984 of approved make to proper grade and alignment, including earthwork in excavation for trenches etc. in all types of soil except soft and hard rock including dewatering till completion of subsequent works, shoring and strutting, if necessary, dressing the sides, leveling, grading and ramming the bottom, jointing the pipes using hot plates as per manufacturer's recommendation, lowering, providing and laying 1:5:10 (1 cement : 5 sand : 10 aggregate) plain cement concrete of minimum 100mm thickness on bottom and side of pipe as directed, connecting the pipes to manholes and grouting the pipes to manhole/valve chamber walls, including supplying and fixing the specials and fittings, such as bends, reducers, tees, elbows, caps etc. conforming to IS:8008 or fabricated from pipes as per specification, supplying and fixing of flanges, fixing of online valves, including fixing of bolts, nuts and gaskets etc. as per specifications, testing, draining of water and cleaning of pipes after testing, backfilling the trenches with select material from available excavated soil including re excavating the deposited soil excavated earlier breaking clods and laying in layers of 15cm compacted thickness, watering and compacting with mechanical means like vibro rammers etc. to 90% standard proctor density as per IS:2720 Part-VII, making good the surface, disposal of surplus earth/ unserviceable material to demarcated area anywhere within the complex limit, cutting of road wherever required, making good the same etc. complete for all depths as per drawings, specification and instruction of Engineer-in- Charge. For the following nominal diameter (mm) Pressure Rating(Kg/Cm2). |  |  |  | 0
21.1 | ( Dia (Internal) - 80 mm, Pressure Rating - 6 Kg/sqcm ) | R. Mtr | 50 |  | 0
22 | Supply and Fixing GI Chain Link Fencing Supplying, fabricating and fixing G.I. chain link fencing with 3.5mm dia. wire, 50x50mm diamond mesh chain link fence fabric conforming to IS:2721 fixed to steel/RCC posts/struts above ground level, including supply of chain link fencing fabric in 1.9 metre wide rolls, steel Frames & Post, stretcher bars, staples, etc. required for fixing the fencing, fixing of chain link fencing between straining post, fixing of bottom in cement concrete 1:2:4 block and Including painting with synthetic enamel etc. including supply and fixing wires, complete as per drawing, specification and direction of Engineer- In- Charge (All materials shall be supplied by contractor). The measurment of chain link fencing shell be on linear basisi for 1.9 m wide fencing fabric. | R. Mtr | 70 |  | 0
23 | CONCENTRINA COIL Providing and fixing Concertina Coil of 600 mm diameter having 50 rounds per 6 m length, (up to 3 Meter Height of Boundary wall) made of high tensile steel wire, securely fixed with G.I. clips to existing barbed wire fencing. The concertina coil shall be supported with angle iron sections of size 50 × 50 × 6 mm, fixed both as cross supports and vertical supports at each pillar, 8 horizontal wire R.B.T. Reinforcement barbed wire, stud tie with G.I. staples and G.I. Clips to retain horizontal, including necessary bolts all complete as per direction of Engineer- In- Charge, with reinforcement barbed tape (R.B.T) / spring core 2.5 m thick wire of tensile strength of 165 KG /sq Mm with tape (0.52 mm thick and weight 43.47 gm/ meter (cost of Ms angle shal be paid separately). | R. Mtr | 70 |  | 0
24 | MISCELLANEOUS STEEL WORKS |  |  |  | 0
24.1 | MS Chequered Plates Supplying and Fabricating are erecting in position at all level and locations bolted , screwed and or/ welded M.S Chequred Plates of any thickness in walk ways , platforms , stairtreads or any other place as directed, etc. cutting to required size shape , making holes , notches , opening of required size , nosing, straightenig if required , making the edges smooth , removing the burrs, fixing , welding , preparation and submission of fabrication drawings and preparing the surface for painting and applying shop primer as per specification after fabrication etc. all complete as specified and directed by EIC. | MT | 1 |  | 0
24.2 | Anchor Bolts Supplying, fabricating , fixing and keeping in position at all level and location Threaded Anchor Bolts of all diameter and nomenclature includings nuts , washers , anchore plate, pipe sleevs etc . Infoundation , column , pedestrals , slabs, beam walletc. or any other place as directed includings handling & Transportation , straightening , if required , turning from relevent size M.S rounds to required diameter , threading , weldings, providing necessary templates and auxiliary dummy structure , if any necessary tying and welding with reinforcement , adjustment of shuttring & reinforcements other fixture , greasing exposed metal surface , covering bolts and packing the sleeves with jute cloth etc. a;; complete as specified and directed by EIC.( Supply of all material in contractor scope) | MT | 0.5 |  | 0
24.3 | MS Metal Inserts Supplying , transportation , storing, fabricating and fixing M.S Metal Insert (with Lugs) of any shape made out of flats, plates, rolled section, pipe, angles etc. providing necessary templates staging cutting, straightening if required bolting , welding as required and embedding in position on both plain and Reinforcement cement concrete members inclusive of adjusting shuttrings & reinforcements / any other fixure , welding where necessary typing and holding to correct level , line and position any auxiliary dummy structure to support the heavy insert , painting exposed surface with a coat of primer as specification all complete for all depth and height as specified and directed . (Supply of All materilas in contractor scope) | MT | 2 |  | 0
25 | SPEED BREAKER Supply and installation of high grade rubber and PVC made Speed Breakers at ingress and egress. Make, Size and Type shall be as per directions of Engineer-In-Charge. | No's | 1 |  | 0
26 | Providing and laying and construction of a rain water drainage channel in brick masonry, including excavation, base preparation PCC M-20 Grade, brickwork Cement Mortar ration (1: 4), plastering, finishing, and curing as per approved drawings and specifications, including shuttring, tampring, ramming, vibrating, curing, etc. all as specified in any shape , position , thickness and finishing the top surface rought or | RM | 260 |  | 0
27 | SUPPLYING AND FIXING IN POSITION ENTRANCE GATE Supplying and fixing in position entrance gate in complex boundary wall fencing manufactured out of steel frame work and square MS bars of 20 mm at 100 c/c and horizontal name plate band at lock rail level suitably hinged with box type steel post embedded in cement concrete i.e. providing the tension bar for smooth operation and locking arrangement etc. complete as per (Design Basis & general technical specification), including painting with two coats of anti-corrosive paint and two coats of approved aluminum/synthetic enamel paint etc. complete as per drawings, specifications and directions of Engineer-in-Charge. |  |  |  | 0
27.1 | 6.0M clear opening width of gate in two panels. (MS Gate) | No's | 1 |  | 0
27.2 | 4.0M clear opening width of gate in two panels. (MS gate) | No's | 1 |  | 0
27.3 | 1.20M clear opening width of gate in one panels. (MS Gate) | No's | 1 |  | 0
28 | PLUMBING AND DRAINAGE Supplying and fixing approved quantity PVC/UPVC below ground and above ground with necessary specials, bends such as Y-junction, T- junction (both single and double) including plugs, shoeS, cowls, jointing with lead caulked joints and testing, cutting in floor,earth work in execution, encasing the pipe in 50 mm Thk, PCC M20, backfilling and removal of surplus earth upto of 50 Mtr. etc. complete as per drawings, specification and direction of Engineer-In-Charge. |  |  |  | 0
28.1 | 100mm dia (All materials including cement supplied by contractor) | Mtr. | 10 |  | 0
28.2 | 80mm dia (All materials including cement supplied by contractor) | Mtr. | 10 |  | 0
28.3 | U/G and A/G G.I Pipe line system- Water Service |  |  |  | 0
| Supplying and laying mild steel galvanised pipes conforming to IS:1239 (heavy grade) and fitting conforming to IS:1239 / ASTM A105 (Galvanized) and as per piping materials specification class including supply of tafflon tapes, white lead etc. cutting the pipe to required length , making threads , earthwork in excavation for trenchess, valve pits etc in all types of soil including hald and soft soil including laying of pipe in trenches , joiniting of pipes and fitting with threads connection , hydrotatics testing of pipe, backfillng the trenches with selected /approved earth fill materials, cutting of roads wherever required, making good the road surface after laying , disposal of surplus earth with in lead of 500 Mtr. etc. including supply of necessary fitting etc. complete as per direction , specificaton and directed by EIC for following Normal size in MM. |  |  |  | 0
| Normal dia -50 MM , pipe class -J2A | Mtr. | 50 |  | 0
28.4 | Supplying and fixing gun metal globe valve conforming to IS: 778, complete as per specification and directed by EIC. (Dia-50 Mm) | NO's | 10 |  | 0
28.5 | Providing and fixing 100 X 100 mm dia gully trap complete with CI grating, CI frame and cover of size 300 mm × 300 mm, including construction of brick masonry chamber in cement mortar 1:4 over M20 grade cement concrete foundation, plastering inside and surface of chamber with cement mortar 1:3, 13 mm average thickness, benching with M20 grade concrete and finished smooth with neat cement slurry, including earthwork excavation, disposal of surplus excavated soil, backfilling with available earth, providing and fixing CI frame and cover, painting CI frame and cover with two coats of approved primer (Chlorinated rubber zinc Phosphate) @40 DFT per coat and finshing painting consists of two coats of chlornited rubber paint @40 DFT two coats of approved finish paint, curing, testing and all incidental works complete as per specifications, drawings and directions of Engineer-in-Charge. |  |  |  | 0
| All material including cement supplied by contractor and (Brick Class-5) | No's | 5 |  | 0
28.6 | Construction of Brick measonary inspection chamber / man holes of 750 mm X 750 mm internal size 1000 MM deep Max in cement mortar 1:4 (1 Cement: 4 Sand) with CI frame and cover 500 MM clear dia (circular Medium duty of grade MD-10) confirming to IS: 1726 fixed on RCC slab of M-30 Grade , necessary excavation , supplying, fixing 4 nos .16 mm dia M.S rungs , M-20 grade foundation concrete 1:3 mortar (1 cement: 3 Sand) plastering of 13 MM average thickness for inside & 16 MM avg thickness of for outside exposed surface , backfilling, disposal of surplus earth upto a lead of 100 Mtr. , benching with M-20 garde cement concrete and rendering smooth with a neat coat of cement slurry , painting the CI frame and cover with two coats of chlorinated rubber zinc phosphate primer @40 DFT per coat and finshing painting consists of two coats of chlorinated rubber paint @40 DFT per coat etc. as directed by Engineer in charge. |  |  |  | 0
| All materials including cement shall be supplied by contractor (Brick Class-5) | No's | 30 |  | 0
29 | Pre- Cast Cover of Tubing Trench Manufacturing, supplying, and installation of pre-cast Heavy-duty tubing trench covers for utility trenches, pipeline protection with grade M-30, which including supply of labour, loading and installation as directed by EIC. |  |  |  | 0
29.1 | Pre Cast cover 600 X 580 X 70 MM with M-30 Grade | No's | 10 |  | 0
29.2 | Pre Cast cover 600 X 580 X 150 MM with M-30 Grade | No's | 50 |  | 0
30 | Dismantling and Demolished Dismantling and Demolishing of building and structure, using manual or heavy machinery, using hand and power tools etc. to demolish structure Cleans up debris and ensures hazardous materials are disposed of correctly as direted by EIC. |  |  |  | 0
30.1 | Brick work Dismantling and Demolished | SQ Mtr. | 10 |  | 0
30.2 | RCC Work Dismantling and Demolished | SQ Mtr. | 10 |  | 0
31 | GROUTING WITH NON-SHRINKABLE COMPOUND |  |  |  | 0
31.1 | Providing and laying manually or by pumping at all positions a ready mix non-shrink cementitious grout of compressive strength specified below for specified works e.g. pipe support, base grouting of rotating equipment and other installation complete in all respects as per scope of work, detailed construction drawings , technical specifications and directions of the Engineer-In-Charge. |  |  |  | 0
31.2 | Having compressive strength of 30 -45 N/mm2 | Per bag of 25 Kg | 20 |  | 0
| 1) Approved makes are ACC, FOSROC, ROFF, SEIKA QUALCRETE. |  |  |  | 0
| 2) Minimum coverage as per manufacturers recommendations shall be applied in absence of actual field consumption data.] |  |  |  | 0
32 | Bore Well Supply , laying , drilling and commissioning of G.I Bore well of 150 MM diameter and upto 100 Mtr. Depth including submersible pump with all accessories , panel wiring and all other work required to make it operational all complete in all respect as per scope of work and directon of the Engineer Incharge | No's | 1 |  | 0
32.1 | Extra over and above for more than 100 M depth | RM | 20 |  | 0
33 | Spectic tank and Soak Pit Construction, supplying, installation, testing and commissioning of spectic tank including soak pit as per standard and IS:2470 Part-I with all necessary accessories like inlet , outlet vent pipe , manhole covers ,rungs etc. including earthwork in excavation in all type of soil except soft and hard rock , backfilling and disposal of surplus earth for all leads, etc. complete as per standards , drawings, specificationand direction of Engineer- In- Charge. |  |  |  | 0
| All materials including cement supplied by contractor (user-10 No's) | No's | 1 |  | 0
34 | Porta Cabin |  |  |  | 0
34.1 | Design Supply, Fabrication, Transportation, Loading, Unloading, Installation, Fixing and commissioning of Porta Cabin of 5.0 Mtr x 4.0 Mtr size as per diagram RGPL-GNET-UK-CGS-ELE-DR-6002. | No's | 1 |  | 0
34.2 | Design Supply, Fabrication, Transportation, Loading, Unloading, Installation, Fixing and commissioning of MS Security Portable Cabin of 6.0 FT x 6FT size | NO's | 1 |  | 0
35 | Supply and installation on terrace, high density polyethylene drinking water circular tank as per IS:12701 and ISI marked including supply and installation of all fittings, cover with suitable locking arrangement, float valve, making necessary holes for inlet, outlet and overflow connection and vent pipe etc. and the base supports for tank including supply of all necessary material all complete as per specifications and directions of Engineer-in-charge. (Sintex or equivalent having valid ISI license) for following capacities. |  |  |  | 0
35.1 | Capacity 1000 Ltr. | No's | 1 |  | 0
| Total Amount |  |  |  | 0
| GST 18 % |  |  |  | 0
| Total Amount Including GST |  |  |  | 0