## Sheet1
Schedule of Rates (SOR)
Subject - Design, Supply, Installation, Testing, Commissioning and 5 years of Comprehensive Operation & Maintenance of LNG Storage & Regasification station at Bikaner & Churu GA
Bidder Name -
Item Sr No | Brief Description | Unit | Quantities | Unit Rate | All applicable taxes & duties | Unit Rate Inclusive of all applicable taxes & duties | Total Price inclusive of all taxes & duties
1 | Bidder Scope includes basic design, development of P&ID, layout as per PESO rules, design based on PESO approval with other applicable guidelines and approval from competent authorities. Scope also include but not limited to design, engineering, procurement of materials, inspection, fabrication, painting and supply of 1 Nos. LNG unloading centrifugal pump for filling up LNG storage tanks from LNG tankers, 2 Nos. 56 KL capacity double-walled vacuum insulated cryogenic LNG storage tank(s), 1 No.s BOGV ( Boil of gas vapouriser) for supplying gas for PNG @4 bar, pressure regulating skid for regulating pressure for PNG supply, odorizing skid, 2 nos.(1 working + 1 stand-by) medium pressure pump, 1+1(standby) No. medium pressure vaporizer along with associated automation, priority panel, canopy, 2 nos.(1 working + 1 stand-by) high pressure reciprocating pump, 1+1(standby) No. high pressure vaporizer along with associated automation, tubing up to cascade and associated auxillary units, priority panel, canopy, LCV filling facility with 1 LCV filling points, supply of air compressor for utility air requirements, supply of all associated valves, fittings, double-walled vaccuum jacketed piping etc. as per scope of work, PJS, Datasheets & Specification etc. attached with tender documents, required to complete the work and whole system as per Indian regulations and codes. Scope shall also include Design and supply of fire fighting system, earthing network, safety interlocks/ instrumentation, emergency push button, safety equipment (such as sand buckets, fire extinguishers, warning signs/ markers etc.) including supply of required materials, system, automation etc. complete in all respects to satisfy all applicable codes and statutory norms in india. Design, supply of all required structural, electrical, instrumentation, PLC & SCADA system etc. to complete the work in all respects shall also be included in the scope. All the consuumables and spares required for installation, testing and commissioning including first fill of Odorisation unit is in bidder scope. The scope is broadly includes but not limited to following equipments and services.
1.1 | Design, Engineering, Fabrication, Supply, Erection, Testing and Commissioning of 1 Nos of LNG unloading pumps of 350 LPM, mounted on the single skid and Integration with the complete system. | LS | 1 Set
1.2 | Design, Engineering, Fabrication, Supply, Erection, Testing and Commissioning of 2 Nos of LNG Stoarage Tank, 56 KL each capacity. | LS | 1 Set
1.3 | Design, Engineering, Fabrication, Supply, Erection, Testing and Commissioning of 1 BOGV ( Boil of gas vapourizer) and 1 low pressure regulating skid with flow meter alongwith all auxiliary units | LS | 1 Set
1.4 | Design, Engineering, Fabrication, Supply, Erection, Testing and Commissioning of 2 (1+1) Medium pressure cryo pumps (70 LPM), to 2 (1+1) Medium pressure vaporiser(2500 SCMH each) and T- connection wth medium to low pressure regulating skid along with flow meter for medium pressure & low pressure alongwith all necessary auxiliary units as described above | LS | 1 Set
1.5 | Design, Engineering, Fabrication, Supply, Erection, Testing and Commissioning of 2 (1+1) High pressure cryo pumps (33 LPM) and 2 (1+1) high pressure vaporisers (1200 SCMH each) alongwith all necessary auxiliary units as described above. | LS | 1 Set
1.6 | Design, Engineering, Fabrication, Supply, Erection, Testing and Commissioning of Odorizing skid (Tank Capacity - 1000 litres) with first fill of odourant and all necessary auxiliary units. | LS | 1 Set
1.7 | Supply and Installation of Fire Hydrant system as per T4S of PNGRB and PESO guidelines. | LS | 1 Set
1.8 | All other safety,PLC,SCADA,electrical etc work required to make the system work as described in the tender document. | LS | 1 Set
Total Amount
2 | Operations - LNG unloading pumps and LNG tanks alongwith all necessary auxiliary units, Medium pressure pumps, vaporiser and medium pressure regulating skid with flow meter alongwith all necessary auxiliary units, Boil of gas vaporiser (BOGV) and Low pressure regulating skid with flow meter alongwith all necessary auxiliary units, High pressure pumps, vaporiser and pressure regulating skid with flow meter alongwith all necessary auxiliary units as described above
2.1 | Operation Charges in 1st year i.e. during Defect Liabilty period | LS | 12
2.2 | Operation Charges in 2nd year i.e. After completion of Defect Liabilty period | LS | 12
2.3 | Operation Charges in 3rd year i.e. After completion of 2nd year | LS | 12
2.4 | Operation Charges in 4th year i.e. After completion of 3rd year | LS | 12
2.5 | Operation Charges in 5th year i.e. After completion of 4th year | LS | 12
Total Amount
3 | Comprehensive AMC including all spare parts & consumables - LNG unloading pumps and LNG tanks alongwith all necessary auxiliary units, Medium pressure pumps, vaporiser and pressure regulating skid with flow meter alongwith all necessary auxiliary units, Boil of gas vaporiser (BOGV) and Low pressure regulating skid with flow meter alongwith all necessary auxiliary units, -High pressure pumps, vaporiser and pressure regulating skid with flow meter alongwith all necessary auxiliary units as described above
3.1 | Comprehensive Maintenance charges for 1st year i.e. during Defect Liabilty period | Machine Month | 12
3.2 | Comprehensive Maintenance charges in 2nd year i.e. After completion of Defect Liabilty period | Machine Month | 12
3.3 | Comprehensive Maintenance charges in 3rd year i.e. After completion of 2nd year | Machine Month | 12
3.4 | Comprehensive Maintenance charges in 4th year i.e. After completion of 3rd year | Machine Month | 12
3.5 | Comprehensive Maintenance charges in 5th year i.e. After completion of 4th year | Machine Month | 12
Total Amount
Gross Amount
NOTES:
a | Prices quoted shall be all inclusive of all local taxes / duties, in-land transportation charges, terminal handling charges and any other applicable charges as defined in tender for DDP: Site. Nothing extra shall be payable by the Purchaser.
b | Bidder to clearly indicate 'Quoted' against line item in the price column.
c | Quoted rates are firm and fixed till complete execution of the entire order.
d | The Prices should be quoted in INR/USD. The bids will be evaluated in INR and conversion rate shall be taken as on the date of bidding.
e | Bidder must quote the price in Schedule of Rates formats only. Bid submitted with changed format / description is liable to be rejected
f | Bidder to specify the make of supply item and must be in operation without hustle from last 5 year from the date of commencement.